## Slide 1
PLC TRAINING PROGRAM · 5-DAY INDUSTRIAL AUTOMATION
Day 1 — Foundations
Full Instructor Teaching Material — Technical Edition
210
minutes total
6
teaching blocks
1
hands-on project
Addressing conventions covered: IEC 61131-3 generic (%I/%Q/%M) · Allen-Bradley tag-based · Siemens (I/Q/M)

## Slide 2
TODAY'S SESSION
Six Blocks, 210 Minutes
1
PLC Basics
Definition, architecture, why it replaced relay panels
15 min
2
PLC Hardware
CPU, power supply, input & output modules
30 min
3
PLC Scan Cycle
Input scan → logic solve → output update
15 min
4
Inputs / Outputs + NO/NC
Wiring, live monitoring, fail-safe contacts
40 min
5
Ladder Logic + Tag Naming
Rungs, AND/OR/NOT, symbolic addressing
60 min
6
Day Project
Motor start/stop with seal-in circuit
50 min
02

## Slide 3
BLOCK 1 · PLC BASICS
What a PLC Actually Is
15 MIN
A purpose-built industrial computer executing a single control program in a deterministic, cyclic loop — reading digital/analog inputs and driving digital/analog outputs each cycle.
COMMON MISCONCEPTION
A PLC is not a general-purpose multitasking OS. It runs one control program in a tight, predictable, repeating loop — hardened against vibration, temperature extremes, and electrical noise via galvanic isolation and conformal-coated boards. A general-purpose PC is not designed or certified for this environment.
CORE ARCHITECTURE
Power Supply
24V DC
CPU
backplane bus
Input Modules
field wiring
Output Modules
actuators / lamps
sensors / switches → input terminals output terminals → actuators / motors
Why it replaced relay panels: relay logic lives in physical wiring — re-wiring a rack for new logic. A PLC's CPU executes the same logic as stored program instructions against an I/O image table in RAM; only the program changes, downloadable in minutes.
03

## Slide 4
BLOCK 1 · PLC BASICS
Key Terms & Where PLCs Show Up
Input
A physical signal (digital or analog) read into the CPU's input image table each scan
Output
A physical signal written from the CPU's output image table to a physical terminal each scan
Program / Logic
The stored instructions (ladder, structured text, function block) solved each scan against the frozen input image
Scan
The full input-scan / logic-solve / output-update cycle — unpacked fully in Block 3
REAL-WORLD USE CASES
Conveyor belts
Start/stop, jam detection via timed no-motion on a speed sensor
Packaging lines
Fill / seal / count cycles
Elevators
Floor sequencing with door interlocks — previews today's interlocking logic
Traffic lights
State-sequenced timing — the full subject of Day 2's project
04

## Slide 5
BLOCK 2 · PLC HARDWARE
CPU & Power Supply
30 MIN
Power supply converts mains AC (100–240V, 50/60Hz) to 24V DC — the near-universal standard for PLC I/O-side power.
WHY 24V DC, SPECIFICALLY
1
Safety margin
Low enough that accidental contact is not lethal under normal conditions, versus mains voltage
2
Universal standard
A 24V DC sensor from one vendor plugs directly into a PLC input module from any other vendor
3
Wiring tolerance
Voltage-drop issues stay manageable at typical field run lengths, unlike lower voltages such as 5V/12V
CPU EXECUTION
Executes the input-scan / logic-solve / output-update loop (full detail in Block 3), and typically exposes onboard diagnostic LEDs: RUN, STOP, FAULT, FORCE.
RUN
STOP
FAULT
FORCE
05

## Slide 6
BLOCK 2 · PLC HARDWARE
Input Modules — Reading the Field
VOLTAGE THRESHOLDS
A digital input module reads 24V DC at a terminal as logic “1” (true); 0V, or below a defined threshold, as logic “0.”
~0-5V = “0”
undefined
~15-24V = “1”
This threshold-based reading — not a clean binary switch — is why proper wiring practice matters: a marginal voltage from a poor connection can produce unreliable, chattering logic state.
MODULE HAS NO WIRING AWARENESS
The module reports raw voltage-derived state — it has no knowledge of whether that terminal is wired to a Normally Open or Normally Closed field switch. That interpretation is entirely a function of field wiring choice (Block 4d) plus how the programmer writes the logic against that bit.
DIGITAL VS. ANALOG — NAME ONLY TODAY
Analog inputs read a continuous voltage/current range rather than a two-state signal. Full coverage on Day 3.
06

## Slide 7
BLOCK 2 · PLC HARDWARE
Output Modules — Three Types
Type | Switches | Response | Mechanism | Notes
Relay | AC or DC | Slower (ms, mechanical) | Electromechanical contact | Robust, galvanically isolates PLC from load; finite mechanical life (~10^5-10^6 cycles)
Transistor | DC only | Fast (µs-ms) | Solid-state switching | No mechanical wear, suited to high-frequency switching (PWM-style); cannot switch AC
Triac | AC only | Fast, solid state | Solid-state AC switching | Common for lamps/solenoids on AC circuits, no mechanical wear
PRACTICAL TAKEAWAY
If a spec sheet says “transistor output module,” that module physically cannot drive an AC contactor coil. Attempting to do so does not simply fail safely — it can damage the output stage. Module type must match the load's electrical requirements before wiring, not after.
07

## Slide 8
BLOCK 3 · PLC SCAN CYCLE
The Loop That Explains Everything
15 MIN
1
INPUT SCAN
Read all physical input terminals, latch values into Input Image Table (IIT). Frozen until next cycle.
2
LOGIC SOLVE
Execute entire program top-to-bottom against the frozen IIT, writing results to Output Image Table (OIT) — not to physical terminals yet.
3
OUTPUT UPDATE
Write the entire OIT to physical output terminals, all at once.
repeat →
TYPICAL SCAN TIME
Commonly low single-digit milliseconds for a small-to-medium program (e.g., 1-10ms), varying with program size, instruction complexity, and CPU class. Not fixed to an exact constant — it shifts cycle to cycle depending on which branches execute.
THE STAKES
This is the single most load-bearing mental model for all debugging this week. Trace one rung through all three phases on the board before moving on.
08

## Slide 9
BLOCK 3 · PLC SCAN CYCLE
Why Scan Time Matters
A GENUINE, QUANTIFIABLE FAILURE MODE
If a physical input pulse (e.g., from a fast-moving proximity sensor) is shorter in duration than one scan time, the PLC can miss it entirely — the signal can go true and false again between two input-scan phases and never appear in the Input Image Table at all.
THE DEBUGGING RULE
Any output that “didn't update when expected” is explained by exactly one of two things:
1
The input hadn't been re-scanned yet when you expected it to reflect a new state
2
The output hadn't been written to the physical terminal yet, because the logic-solve phase for that scan hadn't completed
There is no third category of “the PLC just didn't notice.”
09

## Slide 10
BLOCK 4 · INPUTS / OUTPUTS
Wiring & Verifying I/O
40 MIN
1
Push-Button Input
Walk the terminal strip — channel numbers match module addressing (e.g., channel 0 = %I0.0)
Common vs. signal wire — sourcing/sinking (PNP/NPN) determines what the common terminal references
Never trust a wire without confirming it in software's I/O monitor first
2
Lamp Output
Confirm module type matches load — relay / transistor / triac per Block 2
Ask: “could a transistor-output module drive an AC-rated lamp?” — No, DC only
3
Live Status Monitoring
Open the software's online/monitor view — live I/O state, highlighted per bit
The single most-used debugging tool for the rest of the week
Every student navigates to it themselves, unprompted, before moving on
10

## Slide 11
BLOCK 4 · INPUTS / OUTPUTS
NO vs. NC in Real Circuits
NO
Normally Open
Contact open (no continuity) at rest; closes when actuated.
Reads logic “0” until actuated, “1” while actuated.
NC
Normally Closed
Contact closed (continuity) at rest; opens when actuated.
Reads logic “1” until actuated, “0” while actuated.
WHY THIS DISTINCTION IS ABOUT TO MATTER
NO and NC aren't just wiring trivia — the choice between them is a safety decision. The next block walks through why safety-critical inputs like emergency stops are deliberately wired NC, and what happens electrically when that convention is violated.
11

## Slide 12
BLOCK 4 · INPUTS / OUTPUTS
Why E-Stops Are Wired NC
NC-WIRED E-STOP (correct)
If the wire is cut, the connector unplugged, or the switch fails open — the input reads logic “0,” identical to “button pressed.”
The safety logic responds exactly as if someone pressed the E-stop: the machine stops. The fault produces the same safe outcome as intentional actuation.
NO-WIRED E-STOP (dangerous)
If the wire is cut, the input reads logic “0” — electrically indistinguishable from “not pressed.”
A real wiring fault would go completely undetected while the machine keeps running under a false assumption of safety.
This is a formal, mandated industrial safety design principle — fail-safe design — not a stylistic convention.
12

## Slide 13
BLOCK 5 · LADDER LOGIC + TAG NAMING
Rungs: AND, OR, NOT
60 MIN
Contacts (input conditions, evaluated left to right) sit on the left of a rung; a coil (the result) sits on the right. “Power flow” left to right represents the Boolean evaluation.
AND
|--[ ContactA ]--[ ContactB ]------------( Coil )--|
ST: Coil := ContactA AND ContactB;
Both must be true for current to “flow” to the coil.
OR
|--[ ContactA ]---------------------------( Coil )--|
|--
[ ContactB ]---------------------------|
ST: Coil := ContactA OR ContactB;
Either branch being true energizes the coil.
NOT
|--[/ ContactA ]---------------------------( Coil )--|
ST: Coil := NOT ContactA;
Represented with an NC-style contact symbol on the rung, not a separate instruction.
13

## Slide 14
BLOCK 5 · LADDER LOGIC + TAG NAMING
Symbolic Addressing & Tag Naming
RAW ADDRESSING
%I0.0 %Q0.1
The literal physical terminal address — encodes module/channel position, but carries no semantic meaning six months later.
SYMBOLIC TAGS
Start_PB Motor_Run
A named tag mapped internally to the same physical address, but referenced by name throughout all logic.
PROFESSIONAL NORM
Production-grade programs are almost never written with raw addresses visible in the logic body. %I0.3 tells a future maintainer nothing about what's physically wired there.
COMMENT DISTINCTION
The rung's structure shows what the logic evaluates. A comment records why — e.g. “Motor_Run requires seal-in per motor start/stop pattern; see Block 6.”
14

## Slide 15
BLOCK 6 · DAY PROJECT
Motor Start/Stop with Seal-In
50 MIN
A momentary Start button must energize an output that stays energized after the button releases — the output's own contact wires in parallel with Start, so it “holdes itself in.”
|--[ Start_PB ]----+----------------[/ Stop_PB ]------( Motor_Run )--|
|--[ Motor_Run ]---+ (seal-in contact, in parallel with Start_PB)
ST: Motor_Run := (Start_PB OR Motor_Run) AND NOT Stop_PB;
THE MECHANISM
On the scan Start_PB is pressed, Motor_Run's coil energizes. Next scan, Motor_Run's own contact is now true — the rung stays true even after Start_PB releases. This depends directly on the scan-cycle behavior from Block 3.
Stop wired NC per Block 4d's fail-safe principle — it can break the circuit regardless of Start's state.
15

## Slide 16
BLOCK 6 · DAY PROJECT
Build Walkthrough
1
Plan
5 min
Sketch the seal-in rung on paper first — reasoning about the pattern, not trial-and-error clicking
2
Wire I/O
10 min
Start (NO), Stop (NC per 4d), motor output — module type per Block 2
3
Write the rung
15 min
Implement exactly from the paper sketch
4
Test & debug
15 min
Watch for the common failure: omitting the seal-in contact — motor runs only while Start is held
5
Class review
5 min
Surface the 2-3 most common mistakes actually observed
IF FINISHED EARLY — FORWARD/REVERSE INTERLOCK
Fwd_Run := (Fwd_PB OR Fwd_Run) AND NOT Stop_PB AND NOT Rev_Run; Rev_Run := (Rev_PB OR Rev_Run) AND NOT Stop_PB AND NOT Fwd_Run;
Each direction's rung includes a NOT of the other's own output — whichever energizes first locks out the other on the very next scan. Reappears formally in Day 5's safety-circuit content.
16